## Slide 1: Memory Power Management via Dynamic Voltage/Frequency Scaling
Howard David (Intel)
Eugene Gorbatov (Intel)
Ulf R. Hanebutte (Intel)
Chris Fallin (CMU)
Onur Mutlu (CMU)

## Slide 2: Memory Power is Significant
Power consumption is a primary concern in modern servers
Many works: CPU, whole-system or cluster-level approach
But memory power is largely unaddressed
Our server system*: memory is 19% of system power (avg)
  Some work notes up to 40% of total system power
Goal: Can we reduce this figure?
Chart: Power (W)
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer
System Power | 382.4109 | 375.1503 | 378.5934 | 375.4159 | 379.0878 | 361.1151 | 362.3147 | 335.9757 | 344.1895 | 326.7161 | 334.3453 | 336.6095 | 321.7237 | 317.1999 | 318.8862 | 339.4203 | 323.4101 | 319.6471 | 318.3553 | 324.5306 | 332.3533 | 319.7156 | 329.6844
Memory Power | 79.6873 | 78.6583 | 78.1479 | 78.4162 | 77.6812 | 76.6038 | 74.5227 | 69.1531 | 70.0777 | 65.2711 | 61.2903 | 61.7755 | 59.7297 | 57.1181 | 56.9612 | 58.7216 | 57.0296 | 56.4982 | 55.6446 | 56.6387 | 55.6383 | 54.282 | 57.4416
*Dual 4-core Intel Xeon®, 48GB DDR3 (12 DIMMs), SPEC CPU2006, all cores active. Measured AC power, analytically modeled memory power.

## Slide 3: Existing Solution: Memory Sleep States?
Most memory energy-efficiency work uses sleep states
  Shut down DRAM devices when no memory requests active
But, even low-memory-bandwidth workloads keep memory awake
  Idle periods between requests diminish in multicore workloads
  CPU-bound workloads/phases rarely completely cache-resident
Chart: Sleep State Residency
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer
CKE-low Residency | 0.015242 | 0.018593 | 0.026642 | 0.02386 | 0.048702 | 0.04293 | 0.022079 | 0.048622 | 0.032973 | 0.040465 | 0.040275 | 0.026781 | 0.024897 | 0.027754 | 0.024359 | 0.038534 | 0.03365 | 0.018367 | 0.025418 | 0.037019 | 0.014163 | 0.080439 | 0.030256

## Slide 4: Memory Bandwidth Varies Widely
Workload memory bandwidth requirements vary widely
Memory system is provisioned for peak capacity
   often underutilized
Chart: Memory Bandwidth for SPEC CPU2006
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer
Per-Channel Bandwidth | 6.6379 | 5.8114 | 5.7241 | 5.5465 | 5.2214 | 4.8455 | 4.1329 | 2.8447 | 2.7774 | 1.8864 | 1.1689 | 1.1333 | 0.76345 | 0.33258 | 0.28075 | 0.65757 | 0.32349 | 0.19684 | 0.061357 | 0.2633 | 0.014999 | 0.0075174 | 0.3648

## Slide 5: Memory Power can be Scaled Down
DDR can operate at multiple frequencies  reduce power
  Lower frequency directly reduces switching power
  Lower frequency allows for lower voltage
  Comparable to CPU DVFS
Frequency scaling increases latency  reduce performance
  Memory storage array is asynchronous
  But, bus transfer depends on frequency
  When bus bandwidth is bottleneck, performance suffers
CPU Voltage/Freq. | System Power |  | Memory Freq. | System Power
↓ 15% | ↓ 9.9% |  | ↓ 40% | ↓ 7.6%

## Slide 6: Observations So Far
Memory power is a significant portion of total power
  19% (avg) in our system, up to 40% noted in other works
Sleep state residency is low in many workloads
  Multicore workloads reduce idle periods
  CPU-bound applications send requests frequently enough to keep memory devices awake
Memory bandwidth demand is very low in some workloads
Memory power is reduced by frequency scaling
  And voltage scaling can give further reductions

## Slide 7: DVFS for Memory
Key Idea: observe memory bandwidth utilization, then adjust memory frequency/voltage, to reduce power with minimal performance loss
   Dynamic Voltage/Frequency Scaling (DVFS) for memory
Goal in this work:
  Implement DVFS in the memory system, by:
  Developing a simple control algorithm to exploit opportunity for reduced memory frequency/voltage by observing behavior
  Evaluating the proposed algorithm on a real system

## Slide 8: Outline
Motivation
Background and Characterization
  DRAM Operation
  DRAM Power
  Frequency and Voltage Scaling
Performance Effects of Frequency Scaling
Frequency Control Algorithm
Evaluation and Conclusions
Notes: Briefly go over outline

## Slide 9: Outline
Motivation
Background and Characterization
  DRAM Operation
  DRAM Power
  Frequency and Voltage Scaling
Performance Effects of Frequency Scaling
Frequency Control Algorithm
Evaluation and Conclusions

## Slide 10: DRAM Operation
Main memory consists of DIMMs of DRAM devices
Each DIMM is attached to a memory bus (channel)
Multiple DIMMs can connect to one channel
Memory Bus (64 bits)
/8
/8
/8
/8
/8
/8
/8
/8
to Memory Controller

## Slide 11: Inside a DRAM Device
Bank 0
Sense Amps
Column Decoder
Row Decoder
ODT
Recievers
Drivers
Registers
Write FIFO
Banks
Independent arrays
Asynchronous: independent of memory bus speed
I/O Circuitry
Runs at bus speed
Clock sync/distribution
Bus drivers and receivers
Buffering/queueing
On-Die Termination
Required by bus electrical characteristics for reliable operation
Resistive element that dissipates power when bus is active

## Slide 12: Effect of Frequency Scaling on Power
Reduced memory bus frequency:
Does not affect bank power:
  Constant energy per operation
  Depends only on utilized memory bandwidth
Decreases I/O power:
  Dynamic power in bus interface and clock circuitry reduces due to less frequent switching
Increases termination power:
  Same data takes longer to transfer
  Hence, bus utilization increases
Tradeoff between I/O and termination results in a net power reduction at lower frequencies

## Slide 13: Effects of Voltage Scaling on Power
Voltage scaling further reduces power because all parts of memory devices will draw less current (at less voltage)
Voltage reduction is possible because stable operation requires lower voltage at lower frequency:
Chart: Minimum Stable Voltage for 8 DIMMs in a Real System
| 1333MHz | 1066MHz | 800MHz
 | 1.27 | 1.18 | 1.16
 | 1.35 | 1.24 | 1.2
 | 1.31 | 1.18 | 1.17
 | 1.27 | 1.19 | 1.2
 | 1.22 | 1.13 | 1.1
 | 1.24 | 1.17 | 1.1
 | 1.32 | 1.27 | 1.24
 | 1.26 | 1.26 | 1.21
Vdd for Power Model | 1.5 | 1.425 | 1.35

## Slide 14: Outline
Motivation
Background and Characterization
  DRAM Operation
  DRAM Power
  Frequency and Voltage Scaling
Performance Effects of Frequency Scaling
Frequency Control Algorithm
Evaluation and Conclusions

## Slide 15: How Much Memory Bandwidth is Needed?
Chart: Memory Bandwidth for SPEC CPU2006
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer
Per-Channel Bandwidth | 6.6379 | 5.8114 | 5.7241 | 5.5465 | 5.2214 | 4.8455 | 4.1329 | 2.8447 | 2.7774 | 1.8864 | 1.1689 | 1.1333 | 0.76345 | 0.33258 | 0.28075 | 0.65757 | 0.32349 | 0.19684 | 0.061357 | 0.2633 | 0.014999 | 0.0075174 | 0.3648

## Slide 16: Performance Impact of Static Frequency Scaling
Performance impact is proportional to bandwidth demand
Many workloads tolerate lower frequency with minimal performance drop
Chart: Performance Loss, Static Frequency Scaling
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer
1333->800 | 67.6268 | 44.4197 | 43.6357 | 38.5677 | 33.4097 | 29.7527 | 20.5784 | 11.0576 | 7.6571 | 5.6571 | 4.961 | 2.0771 | 1.3064 | 0.93184 | 0.84334 | 0.60114 | 0.49616 | 0.29464 | 0.045153 | -0.058281 | -0.11397 | -0.21604 | -0.23676
1333->1066 | 28.4478 | 14.9249 | 13.0762 | 12.6744 | 10.7269 | 7.4362 | 4.9122 | 4.0805 | 2.175 | 1.659 | 1.5405 | 0.57676 | 0.95108 | 0.37514 | 0.77451 | 0.22986 | 0.16843 | 0.55862 | -0.00040423 | 0.037662 | -0.010956 | -0.10107 | -0.097227
Chart: Performance Loss, Static Frequency Scaling
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer
1333->800 | 67.6268 | 44.4197 | 43.6357 | 38.5677 | 33.4097 | 29.7527 | 20.5784 | 11.0576 | 7.6571 | 5.6571 | 4.961 | 2.0771 | 1.3064 | 0.93184 | 0.84334 | 0.60114 | 0.49616 | 0.29464 | 0.045153 | -0.058281 | -0.11397 | -0.21604 | -0.23676
1333->1066 | 28.4478 | 14.9249 | 13.0762 | 12.6744 | 10.7269 | 7.4362 | 4.9122 | 4.0805 | 2.175 | 1.659 | 1.5405 | 0.57676 | 0.95108 | 0.37514 | 0.77451 | 0.22986 | 0.16843 | 0.55862 | -0.00040423 | 0.037662 | -0.010956 | -0.10107 | -0.097227
::
::
::
::
::
::
::
::
::
::
:
:
:
:
:
:

## Slide 17: Outline
Motivation
Background and Characterization
  DRAM Operation
  DRAM Power
  Frequency and Voltage Scaling
Performance Effects of Frequency Scaling
Frequency Control Algorithm
Evaluation and Conclusions

## Slide 18: Memory Latency Under Load
At low load, most time is in array access and bus transfer
   small constant offset between bus-frequency latency curves
As load increases, queueing delay begins to dominate
   bus frequency significantly affects latency
Chart: Memory Latency as a Function of Bandwidth and Mem Frequency
| 4278.56666666668 | 4278.56666666668 | 4278.7 | 4277.93333333332 | 4278.033333333326 | 4277.66666666668 | 4277.7 | 4275.76666666668 | 4273.033333333326 | 4268.533333333326 | 4267.533333333326 | 4266.7 | 4258.16666666668 | 4229.43333333332 | 4149.26666666668 | 4122.96666666668 | 4120.400000000001 | 4104.0 | 4092.3 | 4071.566666666663 | 4047.7 | 4006.2 | 3939.2 | 3824.966666666664 | 3652.766666666655 | 3371.766666666655 | 2964.666666666655 | 2576.433333333337 | 2211.0 | 1831.733333333332 | 1573.833333333332 | 1336.9 | 1139.833333333332 | 960.4333333333335 | 829.2 | 721.0666666666666 | 625.2666666666666 | 555.1333333333335 | 498.8333333333333 | 446.2 | 412.9666666666667 | 383.9 | 360.3333333333333 | 339.8 | 325.1333333333335 | 313.4333333333333 | 303.1333333333335 | 295.7666666666667 | 289.8333333333333 | 284.3333333333333 | 280.8999999999999 | 277.9333333333333 | 275.5333333333334 | 273.4333333333333 | 271.9333333333333 | 270.7666666666667 | 269.7 | 268.9666666666667 | 268.366666666667
800MHz | 157.7 | 157.7 | 157.7 | 157.6 | 157.5 | 157.5 | 157.4 | 157.1 | 156.5 | 155.6 | 155.3 | 155 | 153.2 | 147.5 | 135.5 | 132.5 | 132.3 | 130.9 | 129.8 | 127.8 | 125.7 | 121.8 | 116.2 | 109.5 | 102.8 | 96.6 | 91.2 | 87.6 | 84.9 | 82.6 | 81.3 | 80.4 | 80 | 79.7 | 79.5 | 79.5 | 79.5 | 79.6 | 79.6 | 79.6 | 79.7 | 79.8 | 79.9 | 80 | 80 | 80 | 80.1 | 80.1 | 80.1 | 80.1 | 80.1 | 80.1 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
1067MHz | 128.7 | 129 | 128.8 | 128.8 | 128.8 | 128.7 | 128.7 | 128.4 | 127.9 | 126.9 | 126.4 | 126.3 | 124.7 | 120 | 111 | 108.8 | 108.6 | 107.4 | 106.5 | 104.7 | 102.6 | 99 | 94.8 | 90 | 86.3 | 83.3 | 80.7 | 78.9 | 77.6 | 76.5 | 76 | 76.1 | 76 | 76 | 76.1 | 76.2 | 76.3 | 76.5 | 76.6 | 76.7 | 76.8 | 76.9 | 77 | 77 | 77.1 | 77.1 | 77.2 | 77.2 | 77.2 | 77.3 | 77.2 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3
1333MHz | 106.1 | 106.1 | 106 | 105.9 | 105.9 | 105.9 | 105.9 | 105.8 | 105.6 | 105.2 | 104.9 | 104.9 | 104.4 | 101.7 | 95.3 | 93.6 | 93.5 | 92.6 | 91.7 | 90.2 | 88.4 | 85.5 | 82.5 | 79.5 | 77.3 | 75.4 | 73.7 | 72.5 | 71.7 | 71.6 | 70.8 | 70.9 | 70.9 | 70.9 | 71.1 | 71.1 | 71.3 | 71.4 | 71.5 | 71.6 | 71.6 | 71.7 | 71.9 | 71.9 | 71.9 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72.1 | 72.1 | 72.1 | 72.1 | 72.1
800-fit | 77.9804 | 78.5293 | 79.1697 | 79.9269 | 80.8356 | 81.9468 | 83.3363 | 85.1237 | 87.5087 | 90.8509 | 95.8712 | 104.2575 | 121.1014 | 138.0412 | 172.2121
1067-fit | 74.3647 | 74.688 | 75.0516 | 75.4634 | 75.9338 | 76.4761 | 77.1084 | 77.8549 | 78.7498 | 79.8421 | 81.2051 | 82.954 | 85.2795 | 86.7555 | 88.5229 | 93.3616 | 101.3563 | 117.0889 | 132.4882 | 162.3284
1333-fit | 69.6814 | 69.9291 | 70.2007 | 70.4998 | 70.8306 | 71.1987 | 71.6106 | 72.0746 | 72.6015 | 73.2047 | 73.9022 | 74.7181 | 75.6852 | 76.2392 | 76.8498 | 78.2794 | 80.076 | 82.4018 | 83.842 | 85.5309 | 89.9663 | 96.742 | 108.374 | 132.9986 | 167.6296

## Slide 19: Control Algorithm: Demand-Based Switching
After each epoch of length Tepoch:
Measure per-channel bandwidth BW
if BW < T800 : switch to 800MHz
else if BW < T1066 : switch to 1066MHz
else : switch to 1333MHz
Chart: Memory Latency as a Function of Bandwidth and Mem Frequency
| 4278.56666666669 | 4278.56666666669 | 4278.7 | 4277.933333333306 | 4278.033333333316 | 4277.66666666669 | 4277.7 | 4275.76666666669 | 4273.033333333316 | 4268.533333333316 | 4267.533333333316 | 4266.7 | 4258.16666666669 | 4229.433333333306 | 4149.26666666669 | 4122.96666666669 | 4120.400000000001 | 4104.0 | 4092.3 | 4071.566666666658 | 4047.7 | 4006.2 | 3939.2 | 3824.966666666659 | 3652.766666666642 | 3371.766666666642 | 2964.666666666644 | 2576.433333333342 | 2211.0 | 1831.73333333333 | 1573.83333333333 | 1336.9 | 1139.83333333333 | 960.4333333333335 | 829.2 | 721.0666666666666 | 625.2666666666666 | 555.1333333333335 | 498.8333333333333 | 446.2 | 412.9666666666667 | 383.9 | 360.3333333333333 | 339.8 | 325.1333333333336 | 313.4333333333333 | 303.1333333333336 | 295.7666666666667 | 289.8333333333333 | 284.3333333333333 | 280.8999999999996 | 277.9333333333333 | 275.5333333333334 | 273.4333333333333 | 271.9333333333333 | 270.7666666666667 | 269.7 | 268.9666666666667 | 268.366666666667
800MHz | 157.7 | 157.7 | 157.7 | 157.6 | 157.5 | 157.5 | 157.4 | 157.1 | 156.5 | 155.6 | 155.3 | 155 | 153.2 | 147.5 | 135.5 | 132.5 | 132.3 | 130.9 | 129.8 | 127.8 | 125.7 | 121.8 | 116.2 | 109.5 | 102.8 | 96.6 | 91.2 | 87.6 | 84.9 | 82.6 | 81.3 | 80.4 | 80 | 79.7 | 79.5 | 79.5 | 79.5 | 79.6 | 79.6 | 79.6 | 79.7 | 79.8 | 79.9 | 80 | 80 | 80 | 80.1 | 80.1 | 80.1 | 80.1 | 80.1 | 80.1 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
1067MHz | 128.7 | 129 | 128.8 | 128.8 | 128.8 | 128.7 | 128.7 | 128.4 | 127.9 | 126.9 | 126.4 | 126.3 | 124.7 | 120 | 111 | 108.8 | 108.6 | 107.4 | 106.5 | 104.7 | 102.6 | 99 | 94.8 | 90 | 86.3 | 83.3 | 80.7 | 78.9 | 77.6 | 76.5 | 76 | 76.1 | 76 | 76 | 76.1 | 76.2 | 76.3 | 76.5 | 76.6 | 76.7 | 76.8 | 76.9 | 77 | 77 | 77.1 | 77.1 | 77.2 | 77.2 | 77.2 | 77.3 | 77.2 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3 | 77.3
1333MHz | 106.1 | 106.1 | 106 | 105.9 | 105.9 | 105.9 | 105.9 | 105.8 | 105.6 | 105.2 | 104.9 | 104.9 | 104.4 | 101.7 | 95.3 | 93.6 | 93.5 | 92.6 | 91.7 | 90.2 | 88.4 | 85.5 | 82.5 | 79.5 | 77.3 | 75.4 | 73.7 | 72.5 | 71.7 | 71.6 | 70.8 | 70.9 | 70.9 | 70.9 | 71.1 | 71.1 | 71.3 | 71.4 | 71.5 | 71.6 | 71.6 | 71.7 | 71.9 | 71.9 | 71.9 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72.1 | 72.1 | 72.1 | 72.1 | 72.1
800-fit | 77.9804 | 78.5293 | 79.1697 | 79.9269 | 80.8356 | 81.9468 | 83.3363 | 85.1237 | 87.5087 | 90.8509 | 95.8712 | 104.2575 | 121.1014 | 138.0412 | 172.2121
1067-fit | 74.3647 | 74.688 | 75.0516 | 75.4634 | 75.9338 | 76.4761 | 77.1084 | 77.8549 | 78.7498 | 79.8421 | 81.2051 | 82.954 | 85.2795 | 86.7555 | 88.5229 | 93.3616 | 101.3563 | 117.0889 | 132.4882 | 162.3284
1333-fit | 69.6814 | 69.9291 | 70.2007 | 70.4998 | 70.8306 | 71.1987 | 71.6106 | 72.0746 | 72.6015 | 73.2047 | 73.9022 | 74.7181 | 75.6852 | 76.2392 | 76.8498 | 78.2794 | 80.076 | 82.4018 | 83.842 | 85.5309 | 89.9663 | 96.742 | 108.374 | 132.9986 | 167.6296
T1066
T800

## Slide 20: Implementing V/F Switching
Halt Memory Operations
  Pause requests
  Put DRAM in Self-Refresh
  Stop the DIMM clock
Transition Voltage/Frequency
  Begin voltage ramp
  Relock memory controller PLL at new frequency
  Restart DIMM clock
  Wait for DIMM PLLs to relock
Begin Memory Operations
  Take DRAM out of Self-Refresh
  Resume requests
C Memory frequency already adjustable statically
C Voltage regulators for CPU DVFS can work for memory DVFS
C Full transition takes ~20µs

## Slide 21: Outline
Motivation
Background and Characterization
  DRAM Operation
  DRAM Power
  Frequency and Voltage Scaling
Performance Effects of Frequency Scaling
Frequency Control Algorithm
Evaluation and Conclusions

## Slide 22: Evaluation Methodology
Real-system evaluation
  Dual 4-core Intel Xeon®, 3 memory channels/socket
  48 GB of DDR3 (12 DIMMs, 4GB dual-rank, 1333MHz)
Emulating memory frequency for performance
  Altered memory controller timing registers (tRC, tB2BCAS)
  Gives performance equivalent to slower memory frequencies
Modeling power reduction
  Measure baseline system (AC power meter, 1s samples)
  Compute reductions with an analytical model (see paper)

## Slide 23: Evaluation Methodology
Workloads
  SPEC CPU2006: CPU-intensive workloads
  All cores run a copy of the benchmark
Parameters
  Tepoch = 10ms
  Two variants of algorithm with different switching thresholds:
  BW(0.5, 1): T800 = 0.5GB/s, T1066 = 1GB/s
  BW(0.5, 2): T800 = 0.5GB/s, T1066 = 2GB/s
     More aggressive frequency/voltage scaling

## Slide 24: Performance Impact of Memory DVFS
Minimal performance degradation: 0.2% (avg), 1.7% (max)
Experimental error ~1%
Chart: Performance Degradation (%)
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer | AVG
BW(0.5,1) | -0.95209 | 0.072568 | -0.29811 | 0.0093981 | -0.050565 | 0.97321 | 0.42586 | -0.008338 | -0.21795 | 0.3979 | 0.3645 | 0.019834 | 0.78788 | 0.42858 | 1.0132 | 0.23409 | 1.2749 | 0.56002 | 0.12179 | -0.043161 | -0.12696 | -0.33347 | 0.22564 | 0.21212
BW(0.5,2) | 0.13025 | 0.043762 | -0.20782 | 0.61547 | 0.021094 | -0.1219 | -0.12275 | -0.89374 | -0.4216 | 1.694 | 0.58943 | 0.11994 | 0.75334 | 0.57083 | 0.97525 | 0.4459 | 0.51748 | 0.1023 | 0.0021424 | -0.28195 | 0.079867 | -0.41143 | -0.17606 | 0.17495

## Slide 25: Memory Frequency Distribution
Frequency distribution shifts toward higher memory frequencies with more memory-intensive benchmarks
Chart: 
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer
800 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.11 | 0.05 | 0.02 | 0.01 | 0.19 | 0.69 | 0.62 | 0.43 | 0.88 | 0.99 | 0.51 | 0.96 | 0.66 | 1 | 0.99 | 1 | 1 | 0.52
1066 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0.24 | 0.07 | 0.05 | 0.45 | 0.07 | 0 | 0.36 | 0.03 | 0.34 | 0 | 0 | 0 | 0 | 0.23
1333 | 0.99 | 0.99 | 0.99 | 0.99 | 0.97 | 0.85 | 0.95 | 0.98 | 0.99 | 0.56 | 0.25 | 0.33 | 0.13 | 0.05 | 0.01 | 0.13 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0.25

## Slide 26: Memory Power Reduction
Memory power reduces by 10.4% (avg), 20.5% (max)
Chart: Memory Power Reduction (%)
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer | AVG
BW(0.5,1) | 0.29211 | 0.34578 | 0.44199 | 0.34822 | 0.8748 | 0.83769 | 0.69424 | 0.92406 | 0.41246 | 5.5017 | 13.0141 | 10.4221 | 12.0612 | 17.5862 | 19.5006 | 13.5351 | 18.2076 | 18.7821 | 20.2734 | 19.7449 | 20.36 | 20.4849 | 16.2659 | 10.0396
BW(0.5,2) | 0.37761 | 0.35363 | 0.44193 | 0.36777 | 1.0104 | 0.7623 | 0.69426 | 1.0988 | 0.62038 | 7.9845 | 13.4813 | 11.9331 | 13.2872 | 18.0153 | 19.529 | 14.5823 | 18.3953 | 18.8044 | 20.282 | 19.8106 | 20.3438 | 20.4867 | 17.3898 | 10.4371

## Slide 27: System Power Reduction
Chart: System Power Reduction (%)
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer | AVG
BW(0.5,1) | 0.060673 | 0.072568 | 0.091117 | 0.072783 | 0.17924 | 0.17839 | 0.14303 | 0.1902 | 0.083924 | 1.0998 | 2.3903 | 1.9135 | 2.241 | 3.1668 | 3.4948 | 2.3435 | 3.2225 | 3.325 | 3.5471 | 3.4501 | 3.4091 | 3.4753 | 2.8367 | 1.7821
BW(0.5,2) | 0.078745 | 0.074163 | 0.091158 | 0.076972 | 0.20698 | 0.16161 | 0.14275 | 0.22545 | 0.12614 | 1.5984 | 2.4754 | 2.1905 | 2.4668 | 3.245 | 3.4982 | 2.5227 | 3.2486 | 3.3257 | 3.5459 | 3.4608 | 3.4079 | 3.4755 | 3.0304 | 1.8555
As a result, system power reduces by 1.9% (avg), 3.5% (max)

## Slide 28: System Energy Reduction
System energy reduces by 2.4% (avg), 5.1% (max)
Chart: System Energy Reduction (%)
| lbm | GemsFDTD | milc | leslie3d | libquantum | soplex | sphinx3 | mcf | cactusADM | gcc | dealII | tonto | bzip2 | gobmk | sjeng | calculix | perlbench | h264ref | namd | gromacs | gamess | povray | hmmer | AVG
BW(0.5,1) | 0.71305 | 0.019214 | 0.2952 | 0.15728 | 0.28779 | -0.3367 | -0.058787 | 0.27473 | 0.27094 | 1.1959 | 3.144 | 2.669 | 2.4143 | 3.9742 | 4.189 | 3.0917 | 3.5976 | 4.218 | 4.8886 | 4.9311 | 4.8592 | 5.0556 | 3.8008 | 2.3327
BW(0.5,2) | 0.053353 | 0.081996 | 0.26477 | -0.30762 | 0.2339 | 0.28565 | 0.28707 | 0.8941 | 0.46226 | 0.76137 | 3.0168 | 2.9391 | 2.6854 | 3.9763 | 4.1847 | 3.0555 | 4.1452 | 4.5611 | 4.9293 | 5.1499 | 4.7035 | 5.1257 | 4.381 | 2.4291

## Slide 29: Related Work
MemScale [Deng11], concurrent work (ASPLOS 2011)
  Also proposes Memory DVFS
  Application performance impact model to decide voltage and frequency: requires specific modeling for a given system; our bandwidth-based approach avoids this complexity
  Simulation-based evaluation; our work is a real-system proof of concept
Memory Sleep States (Creating opportunity with data placement [Lebeck00,Pandey06], OS scheduling [Delaluz02], VM subsystem [Huang05]; Making better decisions with better models [Hur08,Fan01])
Power Limiting/Shifting (RAPL [David10] uses memory throttling for thermal limits; CPU throttling for memory traffic [Lin07,08]; Power shifting across system [Felter05])

## Slide 30: Conclusions
Memory power is a significant component of system power
  19% average in our evaluation system, 40% in other work
Workloads often keep memory active but underutilized
  Channel bandwidth demands are highly variable
  Use of memory sleep states is often limited
Scaling memory frequency/voltage can reduce memory power with minimal system performance impact
  10.4% average memory power reduction
  Yields 2.4% average system energy reduction
Greater reductions are possible with wider frequency/voltage range and better control algorithms

## Slide 31: Memory Power Management via Dynamic Voltage/Frequency Scaling
Howard David (Intel)
Eugene Gorbatov (Intel)
Ulf R. Hanebutte (Intel)
Chris Fallin (CMU)
Onur Mutlu (CMU)

## Slide 32: Why Real-System Evaluation?
Advantages:
  Capture all effects of altered memory performance
    System/kernel code, interactions with IO and peripherals, etc
  Able to run full-length benchmarks (SPEC CPU2006) rather than short instruction traces
  No concerns about architectural simulation fidelity
Disadvantages:
  More limited room for novel algorithms and detailed measurements
  Inherent experimental error due to background-task noise, real power measurements, nondeterministic timing effects
For a proof-of-concept, we chose to run on a real system in order to have results that capture all potential side-effects of altering memory frequency

## Slide 33: CPU-Bound Applications in a DRAM-rich system
We evaluate CPU-bound workloads with 12 DIMMs: what about smaller memory, or IO-bound workloads?
12 DIMMs (48GB): are we magnifying the problem?
  Large servers can have this much memory, especially for database or enterprise applications
  Memory can be up to 40% of system power [1,2], and reducing its power in general is an academically interesting problem
CPU-bound workloads: will it matter in real life?
  Many workloads have CPU-bound phases (e.g., database scan or business logic in server workloads)
  Focusing on CPU-bound workloads isolates the problem of varying memory bandwidth demand while memory cannot enter sleep states, and our solution applies for any compute phase of a workload
[1] L. A. Barroso and U. Holzle. “The Datacenter as a Computer: An Introduction to the Design of Warehouse-Scale Machines.” Synthesis Lectures on Computer Architecture. Morgan & Claypool, 2009.
[2] C. Lefurgy et al. “Energy Management for Commercial Servers.” IEEE Computer, pp. 39—48, December 2003.

## Slide 34: Combining Memory & CPU DVFS?
Our evaluation did not incorporate CPU DVFS:
  Need to understand effect of single knob (memory DVFS) first
  Combining with CPU DVFS might produce second-order effects that would need to be accounted for
Nevertheless, memory DVFS is effective by itself, and mostly orthogonal to CPU DVFS:
  Each knob reduces power in a different component
  Our memory DVFS algorithm has neligible performance impact  negligible impact on CPU DVFS
  CPU DVFS will only further reduce bandwidth demands relative to our evaluations  no negative impact on memory DVFS

## Slide 35: Why is this Autonomic Computing?
Power management in general is autonomic: a system observes its own needs and adjusts its behavior accordingly
   Lots of previous work comes from architecture community, but crossover in ideas and approaches could be beneficial
This work exposes a new knob for control algorithms to turn, has a simple model for the power/energy effects of that knob, and observes opportunity to apply it in a simple way
Exposes future work for:
    More advanced control algorithms
    Coordinated energy efficiency across rest of system
    Coordinated energy efficiency across a cluster/datacenter, integrated with memory DVFS, CPU DVFS, etc.